SPECIFICATIONS FOR FALSE FLOORING

Supplying of “Kebao” Steel Cement Cavity flooring system (Imported) manufactured by “Kebao International Industrial Group Ltd.” (Shanghai).

Specification of Panel/Tile

Tile Size - 600mm x 600mm tile

Tile thickness - 30mm

Module - HDG-6006 HPL (FS 700)

Point Load - 300 Kg

Uniform Dis. Load (UDL) - 1250 Kg/ M2

Finish: Top covering with high pressure antistatic hot pressed Laminates imported, factory finish in universal white color with grey streamlet pattern. Edge bonded with black conductive PVC beading.

Tile: All steel construction & cavity filled with epoxy mix cement. Top plate 0.70, Bottom plate 0.70mm of steel with grey color powder coated on a continuous line having 64 round embossing to the bottom plate with 100 spot welding to weld top & bottom plate.

Pedestal:  All steel constructions & yellow Zinc plated 25mm Dia pipe pedestal with bottom plate of 100mm x 100mm x 2mm thick. Top plate of 75mm x 75mm x 3mm thick with threaded bolt & 2 nuts for leveling adjustment. (Maximum Height of pedestal for this quote = 600 mm)

Stringer:  Stringers of 1.1mm thick rectangular pipe of size – 22mm (W) x 26mm (Ht.) x 573mm long, 2 holes centre to centre 550mm.

Note: Special feature of the Product:-

- 1. Factory finish laminates (imported).

- 2. Conductive edge beading.

- 3. Solid concrete field, higher load bearing capacity.

4. Special weather coating on back surface of the tiles.

- 5. Fast & accurate installation.

WE REQUEST YOU TO PUT US IN THE APPROVED VENDORS LIST IN THE TENDER DOCUMENT:
Innovative Vastunirman Private Limited - Mr. Ankur Mitna
‘Anurag Apartments’, Flat No. 4,Near Kurtkoti Nursing Home, Kothrud, Pune: 411 038  
Contact no: +91 83800 13600, Telefax: +91 (20) 25280115/16, Website: www.innovastu.com